The proper detail if we go with proper industrial Device

(Actual Device)

Oil Device Gas Data Extraction:

Our Dissolved Gas Analysis (DGA) device is a smart, affordable tool to detect transformer faults early by extracting oil, releasing hidden gases, and measuring them. It works on live (hot) or idle (cool) transformers no shutdown needed. We pull a small oil sample, filter it, pump it through a heated degasser to "pop out" gases (using Henry's Law: warmer oil releases gases better), sense the gases, analyze for faults (like sparks or overheating), and return the oil safely.

Proper Flow (Step-by-Step):

- Connect & Extract: Attach to transformer valve → Open valve → Pump pulls oil (100–200 mL).

- Clean & Heat: Filter dirt → Heat to 70°C if cool (for best gas release).

- Release Gases: In degasser chamber shake/vacuum oil → Gases bubble out.

- Measure: Gases go to sensor chamber → Sensors read values.

- Finish Up: Vent extra gases → Return oil → Controller runs algo → Show results/alerts.

Controller:

- Controller: ESP32 or Raspberry Pi Zero

- Communications/UI: WiFi/Bluetooth module + 2.8" TFT LCD screen

Equipment Required:

| Equipment | Recommended Type/Model | Why We Need It |
| --- | --- | --- |
| Oil Tap Connector | 1/4" NPT brass adapter + quick-connect fitting | Safely hooks to transformer's sampling valve (no leaks on hot oil). |
| Sample Valve | 12V solenoid valve (stainless steel, 100°C rated) | Auto-opens/closes oil flow for safe extraction. |
| Particulate Filter | Inline 10-micron mesh filter (stainless) | Removes dirt/sludge to protect pump and chambers. |
| Flow Pump | 12V peristaltic pump (0.2–1 L/min, e.g., Kamoer or generic) | Gently pulls and circulates oil without contamination. Handles 100°C oil. |
| Degasser Chamber | 200 mL glass vacuum flask + shaker motor (or membrane like PDMS sheet) | Shakes/vacuums oil to release gases into headspace. |
| Heater | 50W PID heating coil + controller (e.g., Inkbird ITC-100) | Warms oil to 70°C if cool or boosts gas release (Henry's Law). |
| Gas Sensor Chamber | Small sealed acrylic box (100 mL, with inlet/outlet ports) | Holds sensors; collects pure gases for accurate reading. |
| Gas Vent/Scrubber | Exhaust valve + activated carbon filter | Safely releases extra gases (no buildup or smell). |
| Oil Return Tubing | 1/4" silicone hose (5m, 150°C rated) + fittings | Sends clean oil back to transformer. |
| Enclosure Case | IP65 waterproof plastic box (30x20x10 cm) | Houses protect everything from dust/weather. |
| Power Supply | 12V/24V DC adapter + rechargeable battery (e.g., 5000mAh) | Powers pump, heaters, sensors portable for field use. |

Sensor required for detect values:

| Sensor | Recommended Type/Model | What It Detects |
| --- | --- | --- |
| Main Gas Sensors (Array) | - H₂: Alphasense H2-A1 or MQ-8 (0–2000 ppm) - CO/CH₄: SPEC Sensors IR or Figaro TGS - Multi-gas: Winsen ZE08 (for C₂H₄/C₂H₂) | Key fault gases: H₂ (sparks), CH₄/CO (heat), etc. |
| Temperature Sensor | DS18B20 waterproof probe (-50 to 150°C) | Oil temp in flow. |
| Pressure Sensor | MPX5700 or BMP280 (0–10 bar) | System pressure. |
| Moisture Sensor | Capacitive oil humidity probe (e.g., HL-1) | Water in oil. |

The primary gases considered in transformer DGA are:

- Hydrogen (H₂)

- Methane (CH₄)

- Ethane (C₂H₆)

- Ethylene (C₂H₄)

- Acetylene (C₂H₂)

- Carbon monoxide (CO)

- Carbon dioxide (CO₂)

Secondary/auxiliary gases often monitored (and sometimes useful) include oxygen (O₂), nitrogen (N₂), carbon disulfide (CS₂) or COS (in systems with sulfur-containing compounds), and traces of other hydrocarbons.

What each gas usually means (origin + typical fault association)

Below are concise notes for each major gas — what creates it and what fault it tends to indicate. These are the conventional interpretations used in IEEE/IEC/CIGRE guidance.

- H₂ (Hydrogen) — produced by electrical discharge/partial discharge (PD) and also by thermal decomposition. Elevated H₂ is commonly the first indicator of PD/energized discharge activity. pstco.net+1

- CH₄ (Methane) — formed by low-temperature thermal degradation (oil/paper up to a few hundred °C) and sometimes PD. Often accompanies H₂. pstco.net+1

- C₂H₆ (Ethane) — formed by low-to-moderate thermal heating of oil/cellulose (higher than CH₄ formation temp). Indicator of low-to-moderate thermal faults. pstco.net

- C₂H₄ (Ethylene) — moderate thermal decomposition (higher temperature than ethane); presence suggests thermal overheating at moderate temperatures. pstco.net

- C₂H₂ (Acetylene) — formed primarily by high-energy arcing (sparks, full arcing). Even small C₂H₂ concentrations are a serious alarm for arcing. pstco.net+1

- CO / CO₂ (Carbon monoxide / dioxide) — mainly from degradation / overheating of paper (cellulose) insulation and aging; CO/CO₂ ratio is used to help distinguish types/extent of paper overheating and degradation. deltaxresearch.com+1

(Other gases like O₂/N₂ inform about oil-preservation integrity and contamination; COS/CS₂ may appear where sulfur compounds are present.)

| Gas | Recommended Sensor / Technology | Approx. Cost | Link |
| --- | --- | --- | --- |
| H₂ (Hydrogen) | Me3-h2 | $50 | Electrochemical Hydrogen Sensor (h2 Sensor) 0~1000ppm - Me3-h2 - Buy Electrochemical Hydrogen Sensor sensor me3-h2 Product on Alibaba.com |
| CH₄ (Methane) | MST-N4 Series | $148 | Mst-n4 Series Infrared Gas Sensor For Co2 Ch4 C2h4 C2h2 C3h8 And More Hydrocarbon,Diverse Range Uart Protocol Ndir Sensor Gas - Buy Sensor Gas for Various Gases Detecting Co2 Ch4 C2h4 C3h8 And More Hydrocarbon ndir Sensor Uart other Sensors air Quality Monitor gas Analyzers gas Detector Product on Alibaba.com |
| C₂H₆ (Ethane) | MST-N4 Series | // | // |
| C₂H₄ (Ethylene) | MST-N4 Series | // | // |
| C₂H₂ (Acetylene) | MST-N4 Series | // | // |
| CO (Carbon monoxide) | MST-N4 Series | // | // |
| CO₂ (Carbon dioxide) | MST-N4 Series | // | // |