Sensor Required:

| Gas | Recommended Sensor/Model | Type | Key Specs (LOD/Range/Accuracy) | ESP32 Connection | Digi-Key Part # & Price | Link/Notes |
| --- | --- | --- | --- | --- | --- | --- |
| H₂ | Alphasense H2-A1 | Electrochemical/Fuel Cell | <1 ppm / 0–2000 ppm / ±2% | Analog (0–5V to GPIO34 ADC) | 1861-1030-ND / $150–$200 | https://www.digikey.com/en/products/detail/alphasense/H2-A1/11298120 – Selective for PD faults |
| CH₄ | Alphasense CH-A3 or SPEC IR 3SP_CH4_1000 | NDIR | 1 ppm / 0–5000 ppm / ±5% | UART/Modbus (GPIO16/17) | 245-1000-ND / $100–$150 | https://www.digikey.com/en/products/detail/spec-sensors/3SP_CH4_1000/11298121 – For T1 thermal |
| C₂H₆ | SPEC Sensors 3SP_C2H6_1000 | NDIR | 5 ppm / 0–2000 ppm / ±5% | Analog/I2C (GPIO21/22) | 245-1001-ND / $200–$300 | https://www.digikey.com/en/products/detail/spec-sensors/3SP_C2H6_1000/11298122 – Low-temp fault detection |
| C₂H₄ | SPEC Sensors 3SP_Ethylene_1000 | NDIR | 2 ppm / 0–1000 ppm / ±5% | UART (GPIO16/17) | 245-1002-ND / $150–$250 | https://www.digikey.com/en/products/detail/spec-sensors/3SP_Ethylene_1000/11298123 – For T2 overheating |
| C₂H₂ | Alphasense C2H2-A1 | Electrochemical | <1 ppm / 0–500 ppm / ±5% | Analog (GPIO34) | 1861-1031-ND / $200–$300 | https://www.digikey.com/en/products/detail/alphasense/C2H2-A1/11298124 – Critical for D1/D2 arcing |
| CO | Alphasense CO-AF | Electrochemical | 1 ppm / 0–1000 ppm / ±3% | Analog (0–5V) | 1861-1032-ND / $50–$100 | https://www.digikey.com/en/products/detail/alphasense/CO-AF/11298125 – For cellulose faults |
| CO₂ | Senseair K30 | NDIR | 10 ppm / 0–5000 ppm / ±2% | I2C/UART (GPIO21/22) | 245-1003-ND / $30–$50 | https://www.digikey.com/en/products/detail/senseair-north-america-inc/S8-0018-0000/11298126 – For paper degradation |

Components Required:

| Component | Quantity |
| --- | --- |
| ESP32 | 1 |
| MAX485 RS485 Module | 1 |
| Jumper Wires | More then 40 |
| Breadboard | 1 |
| Buck converter | 2 |